## Cloud Ceiling Calculator (v1.0)
Cloud Ceiling Calculator
Symbol | Description | Equation | Source | Value | Units
Parameters
A | Maximum Width of Gap Between Clouds or Between Cloud and Wall | - | Given | 12 | inches
B | Ceiling Height | - | Given | 9 | feet
AR | Total Floor Area of Room | - | Given | 800 | ft2
AO | Total Opening Area | - | Given | 160 | ft2
WC | Minimum Width of Ceiling | - | Given | 8 | ft
Solution
X | Gap per Height | X = A / B | NFPA 13-2016 A.8.15.24.1 | 1.3333 | in. gap / ft. ceiling
= (12) / (9)
AO / AR | Is Area of Opening Too Large? | Is AO / AR > 20%? | NFPA 13-2016 8.15.1.2.1.2 | 20 | %
(160) / (800)
ASPRINK | Maximum Sprinkler Protection Area | - | NFPA 13-2016 Table 8.15.24.1 | Not Permitted, Opening Width Too Large for Ceiling Height | ft2
Schematic
Version
1 | 2018-03-27 | Get the latest version at www.meyerfire.com
About
MeyerFire.com is a website dedicated to providing Fire Protection Professionals with tools and resources to do exceptional work. Get other tools like this at www.meyerfire.com.
The views, opinions, and information found here represent solely the author's interpretation and provide no warranty or guarantee of its use or accuracy. MeyerFire does not assume responsibility for use of this tool. Fire protection and life safety systems constitute a critical component for public health and safety. Consult with a licensed professional for proper design and code adherence.
References Used
1 | NFPA 13 | Standard for the Installation of Sprinkler Systems, 2016 Edition
2 | FPRF | Fire Protection Research Foundation, Phase 1 Report
3 | FPRF | Fire Protection Research Foundation, Phase 2 Report
4 | SFPE | Article on Important Changes to NFPA 13
[7 empty] | 5 | 17
[7 empty] | 4 | 15
[7 empty] | 3.5 | 10.5
[7 empty] | 3 | 10
[7 empty] | 2.5 | 9.5
[7 empty] | 2 | 9
[7 empty] | 1 | 0
[7 empty] | A |  | B |  | C |  | C.25 | C.5 | C.75 | D |  | E |  | F
[6 empty] | X-Values | 1 | 1 | 1.4167 | 1.4167 | 2.4167 | 2.4167 | 4.4167 | 6.4167 | 8.4167 | 10.4167 | 10.4167 | 11.4167 | 11.4167 | 11.8333 | 11.8333
[6 empty] | Room Left Wall Left | 0 | 17
[6 empty] | Room Left Wall Right |  |  | 0 | 17
[6 empty] | Room Right Wall Left | [11 empty] | 0 | 17
[6 empty] | Room Right Wall Right | [13 empty] | 0 | 17
[6 empty] | Structure Top | 17 | [13 empty] | 17
[6 empty] | Ceiling Bottom |  |  |  |  | 9 |  |  |  |  | 9
[6 empty] | Ceiling Top |  |  |  |  | 10 |  |  |  |  | 10
[6 empty] | Ceiling Left |  |  |  |  | 9 | 10
[6 empty] | Ceiling Right | [9 empty] | 9 | 10
[6 empty] | Structure Bottom |  |  | 15 | [9 empty] | 15
[6 empty] | Max. Opening Width |  |  | 9.5 |  | 9.5
[6 empty] | Min. Ceiling Width |  |  |  |  | 10.5 |  |  |  |  | 10.5
[6 empty] | Fire | [7 empty] | 2
[6 empty] | Sprinklers spaced normally below ceiling | [6 empty] | 8 |  | 8
[6 empty] | Sprinklers Above Ceiling Required | [6 empty] | 13.875 |  | 13.875
[6 empty] | Sprinklers May be Omitted Above | [7 empty] | -1000